[image: image1.jpg]ROADCROYYN



[image: image2.png]@ yanmar




[image: image3.jpg]







Genset Model
Engine Type
50Hz

kVA    kW
60Hz

kVA   kW
Open

Weight Nett

kg
Canopied

Weight Nett

kg
Open Dimensions (mm)

L     W     H
Canopied Dimensions (mm)

L     W     H

BCY11PSP
3TNE84G1A
10.8    10.8
13.0    13.0
395
485
1300 949 1036
1810 949 1183

BCY17PSP
4TNE84G1A
16.0    16.0
20.0    20.0
640
730
1300 949 1036
1810 949 1183


Single Phase






BCY11PSP






Engine model:
3TNE 84 G1A


1500 RPM
1800 RPM

Number of cylinders
3
Fuel Consumption: l/hr 
3.3
4.1

Cubic capacity : litres (cu.in)
1.496 (91.29)
Heat Rejection to:
9.3 (529)
11.9 (677)

Bore/stroke: mm (in)
84x90  (3.3x3.54)
Exhaust System kW (Btu/min)



Compression ratio:
18:1
Cooling System kW (Btu/min)
7.4 (421)
9.6 (546)

Aspiration:
Natural
Radiated Heat: kW (Btu/min)
6.2 (353)
7.2 (409)

Frequency:
50Hz
60Hz
Exhaust Temperature: ºC (F)
<460 (860)
<485 (905)

Engine Speed
1500 rpm
1800 rpm
Cooling Air Flow: m³/min  (cfm)
19.2 (678)
21.0 (742)

Power at flywheel: kW (hp)
                                       13.5 (18.1)
16.4 (22.0)
Combustion Air: m³/min (cfm)
0.94 (33.3)
1.13 (39.9)

BMEP: kPa (psi) Prime
722 (105)
731 (106)
Exhaust Gas Flow: m³/min (cfm)
2.44 (86.2)
3.03 (107.0)

Piston Speed: m/sec (ft/sec)
4.5 (14.8)
5.4 (17.7)




Fuel Tank Capacity: ltr (UK gal)
55 (12.1)




Single Phase






BCY17PSP






Engine model:
4TNE 84 G1A


1500 RPM
1800 RPM

Number of cylinders
4
Fuel Consumption: l/hr
4.8
5.7

Cubic capacity : litres (cu.in)
1.995 (121.7)
Heat Rejection to:
11.6 (660)
15.3 (870)

Bore/stroke: mm (in)
84x90  (3.3x3.54)
Exhaust System kW (Btu/min)



Compression ratio:
18:1
Cooling System kW (Btu/min)
13.3 (756)
14.0 (796)

Aspiration:
Natural
Radiated Heat: kW (Btu/min)
7.9 (449)
9.5 (540)

Frequency:
50Hz
60Hz
Exhaust Temperature: ºC (F)
<420(788)
<450 (842)

Engine Speed
1500 rpm
1800 rpm
Cooling Air Flow: m³/min  (cfm)
25.3 (893)
32.5 (1148)

Power at flywheel: kW (hp)
                                       19.1 (25.6)
22.9 (30.7)
Combustion Air: m³/min (cfm)
1.29 (45.6)
1.56 (55.1)

BMEP: kPa (psi) Prime
766 (111)
765 (111)
Exhaust Gas Flow: m³/min (cfm)
3.16 (111.6)
4.02 (142.0)

Piston Speed: m/sec (ft/sec)
4.5 (14.8)
5.4 (17.7)




Fuel Tank Capacity: ltr (UK gal)
55 (12.1)




� EMBED PBrush  ���





Performance data





GENERATING 


POWER





SOLUTIONS





�





BCY11PSP


BCY17PSP





PRODUCT REFERENCE SPECIFICATION





TECHNICAL DATA








[image: image1.jpg]

_1068552171

